## Current Annual Costs
Estimated Annual Cost of Nitrous Oxide System - Maintenance & N2O Leakage | [6 empty] | Ver. 2025-07-23
Values are for guidance only and may differ greatly at your site. Adjust assumptions and variables as desired.
Review your med-gas service contract and maintenance costs for more accurate site-specific costs.
Input your data in green cells
N2O System Size for Maintenance Cost Estimation | [5 empty] | Annual Cost Summary
Site | Terminal Units | Zone Valves | Alarm Panels | Manifolds |  | 1. Audit & Repairs | 0
Your Site - Customize | 0 | 0 | 0 | 0 |  | 2. N2O Leakage | 0
Example Site 1 - Large | 190 | 110 | 105 | 1 |  | 3. Occ. Health Audits | 0
Example Site 2 - Medium | 50 | 30 | 30 | 2 |  | Total | 0
Example Site 3 - Small | 3 | 3 | 3 | 1
1. Estimated N2O Annual Audit and Repair Costs
Site | Terminal Units | Zone Valves | Alarm Panels | Manifolds | Repairs | Total Annual Cost
Your Site (N2O only) | 0 | 0 | 0 | 0 | 0 | 0
Example Site 1 - Large | 950 | 550 | 525 | 540 | 5075 | 7640
Example Site 2 - Medium | 250 | 150 | 150 | 1080 | 1400 | 3030
Example Site 3 - Small | 15 | 15 | 15 | 540 | 125 | 710
2. N2O Gas Annual Leakage Cost
litres / tank | 14798 | litres per size 44 tank
Tanks Purchased | 0 | tanks (size 44) per year
Cost | 150 | per tank (size 44)
N2O Purchased | 0 | litres
Cost per litre | 0.010137 | per litre
Leakage Rate | 95% | leakage (typical)
Leakage Cost | 0 | per year
Environmental Cost | 0 | kgCO2e per year from leakage
3. N2O Occupational Health & Safety Audit
Some hospitals do environmental audits, some do not.
# of Audits | 1 | audits per year
Cost per Audit | 0 | per audit
Audit Costs | 0 | per year
Maintenance Assumptions
Typical Maintenance Audit Costs
Terminal Unit | 5 | per
Zone Valves | 5 | per
Zone Alarm | 5 | per
Manifold Compliance
3x Pressure relief devices | 2700 | every 5 years
| 540 | per year amortized
Repair requirements
Repairs | 250 | per repair
Failure rate | 5% | annually
Note on B37: Modify as necessary
Note on C44: Note it may make more sense to consider the full cost instead of the amortized cost for your specific business cases especially if it's coming up soon.
Note on C46: This is just an approximate average for estimation purposes. Note that manifold repairs can quickly run into the $thousands and a complete manifold replacement can be $15k-$30k.

## Decommissioning Costs
Estimated Internal Cost of Decomissioning Nitrous Oxide System | [7 empty] | Ver. 2025-07-23
& Transition to Point-of-Care Delivery
Values are for guidance only and may differ greatly at your site. Adjust assumptions and variables as desired.
Reach out to your local med-gas maintenance to provide a quote if not doing internally.
Input your data in green cells
N2O System Size for Decommissioning and Changes Needed for Transition to Point-of-Care Delivery
Site | Terminal Units | Zone Valves | Alarm Panels | Manifolds | Portable E-tanks | Anesthesia Cart Retrofits | Nitronox Carts
Your Site - Customize | 0 | 0 | 0 | 0 | 0 | 0 | 0
Example Site 1 - Large | 190 | 110 | 105 | 1 | 8 | 0 | 3
Example Site 2 - Medium | 50 | 30 | 30 | 2 | 2 | 4 | 0
Example Site 3 - Small | 3 | 3 | 3 | 1 | 1 | 0 | 0
Estimated Decommissioning & Transition to Point-of-Care Delivery Cost
Site | Terminal Units | Zone Valves | Alarm Panels | Manifolds | Replacement E-tanks | Anesthesia Cart Retrofits | Nitronox Carts | Total Decomissioning Cost
Your Site - Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Example Site 1 - Large | 9500 | 2200 | 1575 | 180 | 3690 | 0 | 12900 | 30045
Example Site 2 - Medium | 2500 | 600 | 450 | 360 | 1110 | 10000 | 0 | 15020
Example Site 3 - Small | 150 | 60 | 45 | 180 | 680 | 0 | 0 | 1115
Decommissioning Assumption and Variables
Standard Costs
Internal Labour Cost | 60 | per hour
Time for terminal unit | 10 | minutes/outlet
Alarm Disabling | 15 | minutes
Manifold Disabling | 180 | minutes
Zone Valve Disabling | 20 | minutes
Outlet Plate/Plug | 40 | /plate&plug
Portable Tank Change - if applicable
N2O e-size tank | 80 | per
Regulator | 250 | per
Dolly | 100 | per
Spare tank holder | 250 | per
Nitronox Cart Replacement | 4300 | if applicable
Anesthesia Cart Retrofit | 2500 | if applicable
Note on C28: Average time for locating, labeling and adding a plug. Increase if removing terminal unit and putting a plate over.
Note on C30: If completely removing and dismantling, budget more time.
Note on C31: Time includes removal of guage and valve. Removal of gauge is not required though.